8.  Simulation of  KSEV operation

The mathematical model of the heated interior has been made using Mathematica® 5.0. The aim was to analyze the cooperation of convection and radiation part of heat transfer. The model has been made for a steady state, i.e.

(1)

takes place for every studied value.

The condition of thermal comfort was added to the system of heat transfer equations and the system was solved for the parameters of thermal comfort as follows:

Tab.1  Input values – thermal comfort parameters

| M | Icl | W | RH | PMV |
| --- | --- | --- | --- | --- |
| 1,2 met | 1,01 clo | 0 W/m2 | 40 % | 0 |

Where:

M - 	human internal heat production  (met, 1,2 met = 70 W/m2),

Icl -	thermal resistance of clothing  (clo, 1,01 clo = 0,157 m2.K/W),

W - 	External Work  (met, W/m2),

RH - 	Relative Humidity  (%),

PMV -     Predicted Mean Vote (-).

Nasledujúci graf zobrazuje možné stavy teploty vzduchu (obr. 1).

Fig. 1 shows the possible combinations of air and mean radiant temperatures.

Fig. 1  mean radiant temperature tr as a function of air temperature  ta for PMV = 0.

List of symbols used in the model; index  stands for ith surface:

tr – 	mean radiant temperature (°C),

ta – 	air temperature (°C),

tei – 	external temperature of  for ith surface (°C),

te – 	temperature of ventilating air (°C),

n – 	the rate of   ventilating air  exchange (h-1),

   -      surface emissivity  (-),

Pfloor –  the power of floor heating  (W),

Pa – 	convective heating power  (W),

Pz – 	the heat loses of the interior  (W).

8.1  Equations of heat transfer and mean radiant temperature

(2)

(3)

(4)

, due to Fig.1.

where:

- specific heat of the air

- air density ()

- convection heat transfer coefficient  obtained from similarity correlations

characteristic dimension of ith surface

- temperature of ith surface

- overall heat transfer coefficient between the ith surface and external air , for the surfaces of internal heating surfaces is valid.

je Stefan-Boltzmann constant

radiation shape factor between ith and jth surface

- radiation heat power from ith surface

- radiation shape factor between ith surface and human body

- ith surface area

- the power supplied to the ith surface (for example floor heating system energy input, energy input of heating radiative panels etc.)

The equations represent thermal comfort, complete conduction, convection and radiation heat transfer balances.

8.2  The results - possible states of heating system operation

The power supplied to the ith surface is divided into two parts: convective and radiation power. In the case outsize  level of Ppodl, mean radiant temperature tr increases, but convection heat transfer can cause the increase of air temperature ta and the conditions of thermal comfort may not be satisfied and PMV > 0 can take place.

To reach the point (tr, ta) from Fig. 1 is in this case possible only by the use of some kind of cooling device to cool the air (Pa<0) to eliminate the influence of too high convection power from the floor.

Analogically  outsize  level of convective power Pa leads to the need of the cooling of the floor (Pfloor<0) if the condition of thermal comfort (point (tr, ta) form Fig. 1) should be satisfied.

To provide the negative power to the surfaces means the need of cooling system installation. The investment and operational costs increase, of course.

Obr. 2  The dependence of Pfloor, and  Pa on the air temperature ta.

(te = -5 °C, n = 0,5)

So, the operation of the system is reasonable for the air temperature  for that Pfloor >0 and Pa > 0 take place, i.e. for air temperature ta app. between 22,8 °C and 25,0 °C.

To satisfy the thermal comfort condition PMV = 0 if for different temperatures impossible without the use of cooling or the floor or the air. This result is unexpected and important for convection-radiation heating systems with floor heating.

8.3  Heat loses of the interior

Energy savings are very important nowadays, so we want to decrease the total heating power as possible. The points (tr, ta) from Fig. 1 are eqvuivalent from the point of view of thermal comfort, but differs regarding the heat loses. Fig. 3 shows the dependence of heat loses  Pz on the air temperature ta.

Fig. 4  The dependence of heat loses  Pz on the air temperature ta

(te = -5 °C and n = 0,5 h-1).

The most important fact is that the increase of the air temperature ta results in the decrease of the heat loses of the interior Pz. It is contradictory with a well-known frequently mentioned contrariwise dependence. The well known rule (decrease of air temperature and increase od mean radiant temperature leads to the decrease of heat loses) is for some situations invalid.

The dependence of heat loses Pz on air temperature ta has been studied for different rates of air ventilation. Near the value n = 3,0 is the pattern of the dependence changes into a usual situation (increase ta causes increase of Pz). Fig. 4. shows the situation.

Fig. 3  The dependence of heat loses  Pz on the air temperature ta

(te = -5 °C and n = 3 h-1).

8.4  Conclusions

The results of made simulations can be recapitulated in the next items:

- It is possible –for given interior parameters- to reach the thermal comfort without the use of cooling system for some interval of  ta only

- The rule that decrease of air temperature and increase od mean radiant temperature leads to the decrease of heat loses) is for some situations invalid. The reason is that the increase of the radiation part of the heat transfer from the floor increases the radiation flows from the floor to the walls and windows. The temperatures of these surfaces increase and it causes the increase of conduction heat loses higher than the decrease of the heat loses by ventilation. The solution of heat transfer and thermal comfort equations only can give the answer if the decrease of  ta gives energy profit.