## Slide 1: Shell-and-Tube Heat Exchangers
Choose of the right TEMA type and decide which stream goes in the tubes
Notes: TEMA is the “Tubular Exchanger Manufacturers’ Association”. Their Standards are almost universally accepted.
Copyright
Hyprotech UK Ltd holds the copyright to these lectures. Lecturers have permission to use the slides and other documents in their lectures and in handouts to students provided that they give full acknowledgement to Hyprotech. The information must not be incorporated into any publication without the written permission of Hyprotech.

## Slide 2: Lecture series
Introduction to heat exchangers
Selection of the best type for a given application
Selection of right shell and tube
Design of shell and tube

## Slide 3: Contents
Why shell-and-tube?
Scope of shell-and-tube
Construction
TEMA standards
Choice of TEMA type
Fluid allocation
Design problems
Enhancement
Improved designs
Notes: “Fluid allocation” means which stream goes on the shell side and which in the tubes

## Slide 4: Why shell-and-tube?
CEC survey: S&T accounted for 85% of new exchangers supplied to oil-refining, chemical, petrochemical and power companies in leading European countries. Why?
Can be designed for almost any duty with a very wide range of temperatures and pressures
Can be built in many materials
Many suppliers
Repair can be by non-specialists
Design methods and mechanical codes have been established from many years of experience
Notes: 85 per cent is a higher figure than in the pie chart in lecture 1. The difference is that the above figure is for the limited range of industries shown while the pie chart is for all industrial applications.

## Slide 5: Scope of shell-and-tube
Maximum pressure
  Shell 300 bar (4500 psia)
  Tube 1400 bar (20000 psia)
Temperature range
  Maximum 600oC (1100oF) or even 650oC
  Minimum -100oC (-150oF)
Fluids
  Subject to materials
  Available in a wide range of materials
Size per unit 100 - 10000 ft2 (10 - 1000 m2)
Can be extended with special designs/materials

## Slide 6: Construction
Bundle of tubes in large cylindrical shell
Baffles used both to support the tubes and to direct into multiple cross flow
Gaps or clearances must be left between the baffle and the shell and between the tubes and the baffle to enable assembly
Shell
Tubes
Baffle

## Slide 7: Shell-side flow

## Slide 8: Tube layouts
Typically, 1 in tubes on a 1.25 in pitch or 0.75 in tubes on a 1 in pitch
Triangular layouts give more tubes in a given shell
Square layouts give cleaning lanes with close pitch
pitch
Triangular
30o
Rotated
triangular
60o
Square
90o
Rotated
square
45o
Notes: Message, use 30 or 600 layouts unless you need to clean the shell side mechanically.

## Slide 9: TEMA standards
The design and construction is usually based on TEMA 8th Edition 1998
Supplements pressure vessel codes like ASME and BS 5500
Sets out constructional details, recommended tube sizes, allowable clearances, terminology etc.
Provides basis for contracts
Tends to be followed rigidly even when not strictly necessary
Many users have their own additions to the standard which suppliers must follow
Notes: Standards are a good thing because they give the designers confidence (they have covered themselves if they have used the standards and then something goes wrong).
They are bad because they can stifle innovation.
The TEMA standards contain recommendations along with the mandatory statements. Some engineers interpret “using TEMA Standards” as meaning following the recommendations as well even though they might not be appropriate to that particular design.
Users of exchangers supplement the TEMA standards with extra rules based on their own experience. This is now thought to be overdone since it may lead to over-expensive designs. The user is, therefore, tending now to give the supplier more freedom but also to emphasise that it is his responsibility.

## Slide 10: TEMA terminology
Letters given for the front end, shell and rear end types
Exchanger given three letter designation
Above is AEL
Shell
Front end
stationary head type
Rear end
head type

## Slide 11: Front head type
A-type is standard for dirty tube side
B-type for clean tube side duties. Use if possible since cheap and simple.
B
Channel and removable cover
Bonnet (integral cover)
A
Notes: Message: use B unless you want to clean inside the tubes frequently.

## Slide 12: More front-end head types
C-type with removable shell for hazardous tube-side fluids, heavy bundles or services that need frequent shell-side cleaning
N-type for fixed for hazardous fluids on shell side
D-type or welded to tube sheet bonnet for high pressure (over 150 bar)
B
N
D

## Slide 13: Shell type
E-type shell should be used if possible but
F shell gives pure counter-current flow with two tube passes (avoids very long exchangers)
E
F
One-pass shell
Two-pass shell
Longitudinal baffle
Note, longitudinal baffles are difficult to seal with
the shell especially when reinserting the shell after
maintenance
Notes: Some users ban the use of F shells because of the problem of sealing the longitudinal baffle against the shell. Some manufacturers have their own systems which can maintain a god seal.

## Slide 14: More shell types
G and H shells normally only used for horizontal thermosyphon reboilers
J and X shells if allowable pressure drop can not be achieved in an E shell
J
H
G
X
Split flow
Double split flow
Divided flow
Cross flow
Longitudinal
baffles
Notes: When G and H shells are used in reboilers (with boiling on the shell side) the longitudinal baffle may be perforated. Its purpose is to help distribute the boiling stream along the length of the exchanger. The seal problem which was noted for F shells is therefore not important.
J shells will have normal segmental baffles as in E shells.
X shells may often have a few inlet and outlet nozzles to help distribute the flow over the length.

## Slide 15: Rear head type
These fall into three general types
fixed tube sheet (L, M, N)
U-tube
floating head (P, S, T, W)
Use fixed tube sheet if T below 50oC, otherwise use other types to allow for differential thermal expansion
You can use bellows in shell to allow for expansion but these are special items which have pressure limitations (max. 35 bar)

## Slide 16: Fixed rear head types
L is a mirror of the A front end head
M is a mirror of the bonnet (B) front end
N is the mirror of the N front end
L
Fixed tube sheet

## Slide 17: Floating heads and U tube
Allow bundle removal and mechanical cleaning on the shell side
U tube is simple design but it is difficult to clean the tube side round the bend
Notes: U-tubes are a simple way of achieving a floating head.
While it is difficult to clean round the bends, some companies offer cleaning devices which can cope with tight bends.

## Slide 18: Floating heads
T
S
Pull through floating head
Note large shell/bundle gap
Similar to T but with smaller shell/
bundle gap
Split backing ring
Notes: Note that the T type requires a large shell and therefore a large shell-to-bundle clearance in order to slide the bundle in and out of the shell. The S type introduces the “split backing ring” which enables the return header to be dismantled and the bundle withdrawn through a smaller diameter shell.
The S type is very common in refinery applications because it enables access to the shell side for maintenance and cleaning without giving a large shell-to-bundle clearance.

## Slide 19: Other floating heads
Not used often and then with small exchangers
P
W
Outside packing to give
smaller shell/bundle gap
Externally sealed floating tube sheet
maximum of 2 tube passes

## Slide 20: Shell-to-bundle clearance (on diameter)
0.5
1.0
1.5
2.0
2.5
0
Shell diameter, m
Clearance, mm
0
150
100
50
Fixed and U-tube
P and S
T

## Slide 21: Example
BES
Bonnet front end, single shell pass and split backing ring floating head

## Slide 22: What is this?
Notes: The students should be able to identify this as a BJM (we are guessing at the M because we cannot see the back end).

## Slide 23: Allocation of fluids
Put dirty stream on the tube side - easier to clean inside the tubes
Put high pressure stream in the tubes to avoid thick, expensive shell
When special materials required for one stream, put that one in the tubes to avoid expensive shell
Cross flow gives higher coefficients than in plane tubes, hence put fluid with lowest coefficient on the shell side
If no obvious benefit, try streams both ways and see which gives best design

## Slide 24: Example 1
Debutaniser overhead condenser
Hot side Cold side
Fluid Light hydrocarbon Cooling water
Corrosive No No
Pressure(bar) 4.9 5.0
Temp. In/Out (oC) 46 / 42 20 / 30
Vap. fract. In/Out 1 / 0 0 / 0
Fouling res. (m2K/W) 0.00009 0.00018
Notes: Ask the students first which stream to put on the shell side and why
Answer: light hydrocarbon because of low fouling and slightly lower pressure. Also condensation works well on the shell side.
Ask what front end type
Answer: A in order to clean easily in the tubes.
Ask what rear head
Answer: fixed head since T small. M could be used or L if access to back end required.

## Slide 25: Example 2
Crude tank outlet heater
Cold side Hot side
Fluid Crude oil Steam
Corrosive No No
Pressure(bar) 2.0 10
Temp. In/Out (oC) 10 / 75 180 / 180
Vap. fract. In/Out 0 / 0 1 / 0
Fouling res. (m2K/W) 0.0005 0.0001
Notes: This one is not so straight forward.
One option is to put the crude oil in the tubes and use an AES. This puts the fouling oil in the tubes and makes cleaning easy.
The use of an S rear head is to allow for differential thermal expansion arising from the large T. However, one can also argue that the shell-side coefficient is so high compared to the tube side, that the tubes is close to the steam condensing temperature (as, of course, is the shell). Hence, a fix head could be used. Provided that access to the shell were never required.
However, because of the high steam pressure you may decide to put this in the tubes. Then you would go for a BEU, and have the tubes on a 90 or 450 layout. This makes it easy to remove the the bundle and clean outside the tubes. Putting the crude outside the tubes would also be likely to give a higher overall coefficient.
It would be worth designing both fully to see which option was the cheapest.

## Slide 26: Rule of thumb on costing
Price increases strongly with shell diameter/number of tubes because of shell thickness and tube/tube-sheet fixing
Price increases little with tube length
Hence, long thin exchangers are usually best
Consider two exchangers with the same area: fixed tubesheet, 30 bar both side, carbon steel, area 6060 ft2 (564 m2), 3/4 in (19 mm) tubes
Length Diameter Tubes Cost
10ft 60 in 3139 $112k (£70k)
60ft 25 in 523 $54k (£34k)
Notes: This is just illustrative since, normally, the overall coefficient will change as the shell diameter is changed, hence the area required to achieve the heat duty will also change. However, this does not negate the point made in the slide.

## Slide 27: Shell thickness
p is the guage pressure in the shell
t is the shell wall thickness
 is the stress in the shell
From a force balance
p
Ds
t
p
t
hence
Notes: Hence the shell thickness increases as the diameter increases thus compounding the higher cost of larger shells.
Referring back to the “crude oil tank heater” example, putting the oil on the shell side will increase the shell thickness because of the higher pressure. However, the shell diameter may decrease with the higher overall coefficient. Against that, the square pitch gives a lower packing density thus tending to increase the shell diameter. Only detailed design and costing will resolve this.

## Slide 28: Typical maximum exchanger sizes
Floating Head Fixed head & U tube
Diameter 60 in (1524 mm) 80 in (2000 mm)
Length 30 ft (9 m) 40 ft (12 m)
Area 13 650 ft2 (1270 m2) 46 400 ft2 (4310 m2)
Note that, to remove bundle, you need to allow at least as much length as the length of the bundle

## Slide 29: Fouling
Shell and tubes can handle fouling but it can be reduced by
keeping velocities sufficiently high to avoid deposits
avoiding stagnant regions where dirt will collect
avoiding hot spots where coking or scaling might occur
avoiding cold spots where liquids might freeze or where corrosive products may condense for gases
High fouling resistances are a self-fulfilling prophecy
Notes: If you specify a very high fouling resistance, the clean exchanger will over perform when fist installed. The operators will then throttle back on the flow of the service stream thus helping to promote fouling. Then the designer can say, “I told you it has a high fouling.”

## Slide 30: Flow-induced vibration
-
Velocity
Velocity
Resonance
Instability
Two types - RESONANCE and INSTABILITY
Resonance occurs when the natural frequency coincides with a resonant frequency
Fluid elastic instability
Both depend on span length and velocity
Tube displacement
Notes: A resonance would occur if the tube natural frequency corresponded with the vortex-shedding frequency.
Usually, instabilities are worse because and can lead to failures in a short time.

## Slide 31: Avoiding vibration
Inlet support baffles - partial baffles in first few tube rows under the nozzles
Double segmental baffles - approximately halve cross flow velocity but also reduce heat transfer coefficients
Patent tube-support devices
No tubes in the window (with intermediate support baffles)
J-Shell - velocity is halved for same baffle spacing as an E shell but decreased heat transfer coefficients
Notes: Pictures illustrating some of these arrangements are show on the next slide.

## Slide 32: Avoiding vibration (cont.)
Inlet support
baffles
Double-segmental baffles
No tubes in the window - with intermediate support baffles
Tubes
Windows
with no tubes
Intermediate baffles

## Slide 33: Shell-side enhancement
Usually done with integral, low-fin tubes
  11 to 40 fpi (fins per inch). High end for condensation
  fin heights 0.8 to 1.5 mm
Designed with o.d. (over the fin) to fit into the a standard shell-and-tube
The enhancement for single phase arises from the extra surface area (50 to 250% extra area)
Special surfaces have been developed for boiling and condensation

## Slide 34: Low-finned Tubes
Flat end to go into tube sheet and intermediate flat portions for baffle locations
Available in variety of metals including stainless steel, titanium and inconels

## Slide 35: Tube-side enhancement using inserts
Spiral wound wire and twisted tape
Increase tube side heat transfer coefficient but at the cost of larger pressure drop (although exchanger can be reconfigured to allow for higher pressure drop)
In some circumstances, they can significantly reduce fouling. In others they may make things worse
Can be retrofitted
Twisted tape

## Slide 36: Wire-wound inserts (HiTRAN)
Both mixes the core (radial mixing) and breaks up the boundary layer
Available in range of wire densities for different duties
Notes: This picture shows colour dyes clinging to the wall without mixing with the main stream until they hit the wire matrix and become mixed.

## Slide 37: Problems of Conventional S & T
Zigzag path on shell side leads to
Poor use of shell-side pressure drop
Possible vibration from cross flow
Dead spots
  Poor heat transfer
  Allows fouling
Recirculation zones
  Poor thermal effectiveness, 
Notes: These are illustrated on the next slide

## Slide 38: Conventional Shell-side Flow

## Slide 39: Shell-side axial flow
Some problems can be overcome by having axial flow
Good heat transfer per unit pressure drop but
  for a given duty may get very long thin units
  problems in supporting the tube
RODbaffles (Phillips petroleum)
introduced to avoid vibrations by providing additional support for the tubes
also found other advantages
  low pressure drop
  low fouling and easy to clean
  high thermal effectiveness
Notes: RODbaffles are really grids to support the tubes. Picture on next slide.

## Slide 40: RODbaffles
Tend to be about 10% more expensive for the same shell diameter
Notes: The grids are offset so that it takes a set of 4 grids to support a given tube on the top, bottom left and right.

## Slide 41: Twisted tube (Brown Fintube)
Tubes support each other
Used for single phase and condensing duties in the power, chemical and pulp and paper industries
Notes: Despite the fact that the tubes touch in places, there are lines of sight through the bundle in many places which allows for cleaning.

## Slide 42: Shell-side helical flow (ABB Lummus)
Independently developed by two groups in Norway and Czech Republic
Notes: Note that the shell-side flow near the shell will have different heat transfer characteristics than flow near the centre of the bundle. This make this exchanger unsatisfactory for high  duties.

## Slide 43: Comparison of shell side geometries