## Slide 1: SHELL-AND-TUBE HEAT EXCHANGERS
P M V Subbarao
Professor
Mechanical Engineering Department
I I T Delhi
An Engineering Solution to the Crisis of Massive Volume Requirements…
A Complex Blend of Simple Ideas….

## Slide 2: A crisis of More Area than the Required Heat Exchanging Surface Area

## Slide 3: Why a Shell and Tube Heat Exchanger?
Shell and tube heat exchangers are the most widespread and commonly used basic heat exchanger configuration in the process industries.
The reasons for this general acceptance are several.
The shell and tube heat exchanger provides a comparatively large ratio of heat transfer area to volume and weight.
It provides this surface in a form which is relatively easy to construct in a wide range of sizes.

## Slide 4: Better Concurrence….
It is mechanically rugged enough to withstand normal shop fabrication stresses, shipping and field erection stresses, and normal operating conditions.
The shell and tube exchanger can be reasonably easily cleaned, and those components most subject to failure - gaskets and tubes – can be easily replaced.
Shop facilities for the successful design and construction of shell and tube exchangers are available throughout the world.

## Slide 5: Simple Shell & Tube Heat Exchanger

## Slide 6: Inner Details of S&T HX

## Slide 7: Components of STHEs
It is essential for the designer to have a good working knowledge of the mechanical features of STHEs and how they influence thermal design.
The principal components of an STHE are:
shell; shell cover;
tubes; tubesheet;
baffles; and nozzles.
Other components include tie-rods and spacers, pass partition plates, impingement plate, longitudinal baffle, sealing strips, supports, and foundation.

## Slide 8: Types of Shells

## Slide 9: Fixed tube sheet

## Slide 10: U-Tube STHE

## Slide 11: Floating Head STHE TEMA S

## Slide 12: Floating Head STHE TEMA T

## Slide 13: A New Part…. Only for SHTE

## Slide 14: Cross Baffles
Baffles serve two purposes:
Divert (direct) the flow across the bundle to obtain a higher heat transfer coefficient.
Support the tubes for structural rigidity, preventing tube vibration and sagging.
When the tube bundle employs baffles,
the heat transfer coefficient is higher than the coefficient for undisturbed flow around tubes without baffles.
For a baffled heat exchanger the higher heat transfer coefficients result from the increased turbulence.
the velocity of fluid fluctuates because of the constricted area between adjacent tubes across the bundle.

## Slide 15: Types of Baffle Plates : Segmental Cut Baffles
The single and double segmental baffles are most frequently used.
They divert the flow most effectively across the tubes.
The baffle spacing must be chosen with care.
Optimal baffle spacing is somewhere between 40% - 60% of the shell diameter.
Baffle cut of 25%-35% is usually recommended.

## Slide 16: Types of Baffle Plates
Triple Segmental Baffles
Double Segmental Baffles
The triple segmental baffles are used for low pressure applications.

## Slide 17: Types of Baffle Plates

## Slide 18: Types of Baffle Plates
Disc and ring baffles are composed of alternating outer rings and inner discs, which direct the flow radially across the tube field.
The potential bundle-to-shell bypass stream is eliminated
This baffle type is very effective in pressure drop to heat transfer conversion

## Slide 19: Types of Baffle Plates
In an orifice baffle shell-side-fluid flows through the clearance between tube outside diameter and baffle-hole diameter.

## Slide 20: Therm-Hydraulic Analysis of Heat Exchanger
Initial Decisions.
Tube side Thermal Analysis.
Thermal analysis for Shell side.
Overall Heat Transfer coefficient.
Hydraulic Analysis of Tube side.
Hydraulic Analysis of Shell side.

## Slide 21: Fluid Allocation : Tube Side
Tube side is preferred under these circumstances:
Fluids which are prone to foul
The higher velocities will reduce buildup
Mechanical cleaning is also much more practical for tubes than for shells.
Corrosive fluids are usually best in tubes
Tubes are cheaper to fabricate from exotic materials
This is also true for very high temperature fluids requiring alloy construction
Toxic fluids to increase containment
Streams with low flow rates to obtain increased velocities and turbulence
High pressure streams since tubes are less expensive to build strong.
Streams with a low allowable pressure drop

## Slide 22: Fluid Allocation : Shell Side
Shell side is preferred under these circumstances:
Viscous fluids go on the shell side, since this will usually improve the rate of heat transfer.
On the other hand, placing them on the tube side will usually lead to lower pressure drops. Judgment is needed.
Low heat transfer coefficient:
Stream which has an inherently low heat transfer coefficient (such as low pressure gases or viscous liquids), this stream is preferentially put on the shell-side so that extended surface may be used to reduce the total cost of the heat exchanger.

## Slide 23: Options for Shell-Side Thermal Analysis
Kern's integral method
Bell-Delaware method
Stream analysis method
Recent Methods

## Slide 24: Kern Method of SHELL-AND-TUBE HEAT EXCHANGER Analysis

## Slide 25: Knowledge for Solving True Industrial Problems : Donald Q Kern
True believer of providing knowledge for use of solving run-of-the-mill problems.
Donald Q. Kern Award: AIChE.
In honor of Donald Q. Kern, pioneer in process heat transfer, the Division recognizes an individual's expertise in a given field of heat transfer or energy conversion.
There is no true flow area by which the shell-side mass velocity can be computed.
Fictitious values for equivalent diameter and mass velocity are to be defined.
These are borne out by experiment.

## Slide 26: Flow Past Tube Bundles : Outside Film Coefficient

## Slide 27: Kern’s Integral Method
The initial attempts to provide methods for calculating shell-side pressure drop and heat transfer coefficient were based on experimental data for typical heat exchangers.
One of these methods is the well-known Kern method, which was an attempt to correlate data for standard exchangers by a simple equation analogous to equations for flow in tubes.
This method is restricted to a fixed baffle cut (25%) and cannot adequately account for baffle-to-shell and tube-to-baffle leakages.
Although the Kern equation is not particularly accurate, it does allow a very simple and rapid calculation of shell-side coefficients and pressure drop to be carried out

## Slide 28: Major Steps in Design
Initial Decisions.
Tube side Thermal Analysis.
Thermal analysis for Shell side flow.
Overall Heat Transfer coefficient.
Hydraulic Analysis of Tube side.
Hydraulic Analysis of Shell side.

## Slide 29: Initial Decisions
Spatial allocation of fluid.
Determination of flow velocity.
Initial guess for number of tubes.
Correction for standard tube diameter.
Effect of number of tubes on tube length….