Introduction

The transition of power systems from central planned, regulated and controlled by a government did not have only positive outcomes: an increase in power flow to stability limits, that happens far more often than before, with combination of unpredictable atmospheric conditions and failures of elements of power system caused in recent years a few big and small blackouts.

In August of 2003 north-east part of the USA and neighboring parts of Canada suffered a huge power outage. According to some estimations over 50 million people did not have electricity. The blackout was caused by droop of power lines due to the thermal effect of overload, that eventually touched tree which causes the short circuit. Furthermore, the heatwave increased power demand, and the rest of the transmission lines had to be disconnected because of overload. Consequently, a few power plants operation stopped and the whole area underwent a blackout. During same smaller incidents happened in Sweden and eastern part of Denmark.

An overload of an electric grid happens frequently, moreover abnormal operation states occurs more often than before deregulation of electricity markets.  Besides, an increase in installed capacity of so-called renewable power sources and their government support over conventional power plants (like Nuclear and Coal) is one of the factors contributing to the decrease of power system’s stability under high demand.

The previous experience shows that power outages in wide areas might happen in any time during any operational state of a power system, therefore all operations require more reliable and advanced means of monitoring. Moreover, capabilities of the monitoring systems must meet requirements for synchronized measurements of dynamics of an electric grid. Application of PMU with GPS to synchronize with UTC (Universal Coordinated Time) was proposed and latter introduced in power systems. It established a concept of synchronized measurements of phasors also called synchrophasor [citation].

The overall improvement of power system stability can be achieved by introduction of PMUs because data acquired using PMU might be used for check of state estimators. Correct estimation of state is crucial for Energy management system which does contingency analysis, regulate stability and optimize power flow.

However, for enhancement of state estimation the phasor measurements must have high precision. Hence, many researchers concern with accurate phasor calculations, with respect to variable frequency.

In authors opinion some make incorrect assumption that fundamental frequency in power system is 50. Firstly electric grid is always in dynamics and secondly due to some previously mentioned reasons in modern power systems fundamental frequency often has relatively large deviation from nominal value. (lze vlozit obrazek distribuce merene frekvenci v siti)

Proposed method for frequency estimation.

In this section, the proposed method is described using a continuous signal. Later the same approach will be demonstrated on a discrete signal. Let  be a continuous function representing examined signal with a period T. Thus, the mean value m of the function on the interval L is as follows:

Since, in this case, the examined function is periodic, for the  the value of m will be the same for any start point . Furthermore, the later implies with not equal to m varies for different  i.e is dependent on  .

The proposed approach can be divided into several simple mathematical operations. Firstly, for chosen interval of , calculate the mean values for . Then compute variance of acquired results. Find the  with regards to the minimum of variance.

Note, the method utilizes variance, which fundamentally indicates variability in data. Therefore, for the true T of a periodic function variance should be zero. Let us write it more rigorously in terms of equations.

Hereafter instead of  will be used , where   is a correction coefficient of initial guess  of the period . The mean value of the function  on the interval :

The variance of mean values is as follows:

where  is a time interval chosen for assessment of variance and mm is the mean of m throughout the interval.

Final step of the algorithm is to find minimum of the objective function .

It is worth mentioning that  is an elective constant, which defines length of examined interval. Clearly for finding the true period of a periodic function an interval should be at least long as true period. However, it is impossible to know for sure the period of a function, thus taking longer interval avoids possible issues. The figure shows how the value of  affects the steepness of the function, therefore the optimization problem as well. Larger  is beneficial for precision and avoiding mistake with initial guess of the period of examined function; however, it requires more computational effort.

Application to discrete signals

This section outlines the application of the proposed algorithm to discrete or sampled signals. Since, in practice engineers deals with non-continuous signals. Let us now describe systematically the method application to sampled signals.

The period of a sampled signal is represented by number of samples. It should be noted, that it is one of the crucial problems since it is improbable to sample signal with integer number of samples per true period.

In this case, the initial guess is number of samples per period . Furthermore, the set of possible samples per period is , where  are reasonably chosen depending on the application. Also, an interval for estimation of frequency is . The mean of the discrete signal for n samples with starting sample j is as follows:

Where  is ith sample.

The variance of the obtained mean values is:

Where  is:

Note, that function  is defined for positive integers only. The last step of the algorithm is to find minimum of the function. Nevertheless, optimizing the objective function for integers will not yield precise solution. Hence, the authors chose approximation by parabola around minimum point. To do so, the function  must be evaluated for range of possible n. The result is a set of pairs . Then choose 3 pairs from the obtained set with smallest values of , and approximate them by parabola. Finally, calculate the position of the vertex. In order to decrease computational effort, the position of vertex can be found by using following formula:

The  represents estimated number of samples per period. Hence, the period is .

Compliance with IEEE standard Synchronophasor measurements.

This section provides examples of agreement of the proposed approach for consequent application to phasor estimation. The standard [citation] defines different requirements for phasor measurement units, testing conditions, like maximum THD etc. Also, it specifies measure for evaluation of compliance. The method was implemented using Wolfram Mathematica, and then the testing conditions defined by standard were recreated in computer simulation. The experiments confirmed compliance with IEEE standard.

The authors chose to provide results of the Dynamic compliance (Measurement bandwidth) test [citation], because in their opinion it is the hardest requirement to meet. The test essentially consists of feeding the PMU algorithm a signal with modulated amplitude and phase angle. Hence, mathematically signal is represented by following formula:

where A is the amplitude, - coefficient of amplitude modulation,  is phase angle modulation factor,  is fundamental frequency an electric grid and  is modulation frequency.

The standard defines following test conditions, that were fulfilled, 100% rated signal magnitude and nominal frequency. Also,  and   are equal to 0.1. Authors, tested the algorithm for different modulation, but here the results are provided for the worst possible case 5 Hz.

It should be noted that the main measure of the compliance is TVE (Total Vector Error), which quantify difference between theoretical value of phasor with obtained by measurement. The definition of TVE is as follows:

Where  is nth calculated phasor and  is corresponding true phasor value, indices r and I represent real and imaginary part respectively.

The figure clearly shows that proposed approach complies with requirements of IEEE standard. Moreover, margin of safety remains quite substantial, so proposed method can cope with even higher interference.

Application to signals with noise.

For comparison of the proposed method with existing approaches to estimation of fundamental frequency, numerous simulations were conducted using Wolfram Mathematica.

The signals were generated with known frequency and amplitudes of higher harmonics.

To the sampled data a noise was added, using pseudo-random numbers with a Gaussian distribution and zero mean value. The consideration of zero mean value is motivated by the investigation of the proposed method to power systems, where signals are outputs of measurement transformers of current and voltage. Hence, in Harmonic steady state, the mean value will be zero and noise is voltage induces by electromagnetic interference from switching processes nearby. It is worth mentioning that a DC component does not affect the precision of the proposed method. Gaussian distribution is used since low induced noise voltages are more probable than high. (Distant sources of noise are numerous compared to close.)

Compared method of frequency estimation were always 100 times applied to data with noise, generated for each time. Then from the results, the relative error and maximum absolute error were calculated.

The following methods were chosen for comparison:

- The proposed approach

- Zero crossing algorithm, where data at fist are filtered using Moving Average. Then samples with an absolute value of 1% of the difference between maximum and minimum values of the signal, are found and grouped. Each group represents an edge of the signal. Therefore, those groups of samples are approximated by lines, then times of lines zero crossings are computed. This approaches could be practically used for signals with noise, without filtering.

- Method of frequency estimation using discrete Fourier transform implemented in Wolfram Mathematica 11.2.

For simulation, which results are displayed in figure 111, the following conditions were chosen:

- sampling frequency 48000 samples per second, hence 980 samples per nominal period of a signal with fundamental frequency 50 Hz

- Frequency is 1.0456 times higher than nominal, first harmonic with amplitude 1 V (no other harmonics were represented in the signal)

- deviation of Gaussian distribution was chosen to be 0.4 V

- kNoise is coefficient of generated noise, meaning every batch of generated noise were multiplied by an exponential distribution, which consists of 21 values from 0.001 to 1.2 including.

- Data size was 4.8 times of the nominal period

It should be noted, that the size of data had to be big enough for estimnation of frequency using FFT, otherwise this mehtod is infeasible.

Figure 11 shows the results of the simulation with the following parameters:

- sampling frequency 48000 samples per second, hence 980 samples per nominal period of a signal with fundamental frequency 50 Hz

- Frequency is 1.0456 times higher than nominal. Signal had first, third, seventh and eleventh harmonics with amplitudes 1 V, 0.1 V, 0.05 V and 0.01 V respectively.

- The standard deviation of Gaussian distribution was chosen to be 0.4 V

- kNoise is coefficient of generated noise, meaning every batch of generated noise were multiplied by an exponential distribution, which consists of 21 values from 0.001 to 1.2 including.

- Data size was 4.8 times of the nominal period