Tomáš Novotný, Jan Kyncl

H Matrix Fault Location Method–
Study of the Phasor Measurement Error Influence

Abstract

The paper shows a new method how to find the fault admittance in the method of fault location using H-matrices by a finite algorithm. The use of the method has been shown on an example of fault location using input phasors as exact values with added noise of Gaussian probability distribution.

Introduction

H-matrices are used in situations where cascading system occurs because of simple fact that H-matrix describing system in cascade is a product of matrices describing parts of the cascade. In electrical power engineering we can use H-matrices to include wave phenomena on HW lines without differential equations or to locate faults.

The influence of disturbances and noise on measurement accuracy on fault location method has been studied in [1], where we simulated fault location process by numerical modeling of next steps: Determination of HV lines parameters, harmonic steady state solution, transient calculation, adding the noise to the data, data smoothing and filtering, determination of phasors and fault location using obtained phasors. Considered analysis is good for the design of whole system for fault location in which time-depended values of voltages and currents and parameters of the line are available and type and position of the fault is the output.

There are some providers of phasor metering systems for electrical power grids, so the question of the possibility of the use sets of phasors with given inaccuracy lies ready to hand.

- Principle of the method

Let’s assume situation according to Fig. 1.

Let’s assume that phasors  and in the case of more than two wires should be replaced by vectors of input and output phasors. H matrix is a regular square matrix of relevant order. H matrix describing the whole double line system is a product of mth power of H matrix describing an element of line system for chosen division, H matrix describing the fault and (n-m-1)th power of H matrix describing an element. Equation (3) shows the principle. The H matrix describing the fault is a function of unknown admittance of the fault.

(1)

The task is to determine for chosen line division n index of faulted section m and the type of the fault. In this paper we study the fault caused by added admittance between two wires of the line.

Be vectors of input and output voltages and currents and . We choose  and for each m we find as the complex number that gives the best compliance of (1).

So, for given m we can understand (1) as

Figure 1. Fault location situation.

(2)

where A and C  are regular matrices of complex numbers, and  vectors of complex numbers and  is a matrix describing the fault and for our chosen type of fault can be rearranged as

(3)

where E is identity matrix of the same matrix rank as A and C and  D is a matrix of complex numbers, and  are vectors of phasors obtained from phasor metering system.

Having denoted

(4)

and

(5)

where the star means complex conjugation operator and dot the dot product of vectors, we search for such as is minimal.

Providing (3) we demonstrate that finding can be obtained by a finite process.

Be the real part of complex number  and , so if we use j for the imaginary unit we can express in terms of its real and imaginary part:

(6)

Be matrix rank of A, B, C and D and the dimension of vectors and denoted as N.

Using a routine notation of vector as a sum of unit vectors multiplied by respective coordinates, i.e. , involving (3) into (4) we obtain:

(7)

where are complex numbers. Similarly

(8)

Hence

(9)

where are complex numbers; now we can evaluate :

(10)

We denote:

and hence:

(11)

We can expand the last term in (11), but we know, that  and .

So, the last term must be real number and a linear form of variables.

Finally we see that can be expressed as:

(12)

and the minimum is then

.

Be , hence:

(13)

Equation (12) says us that  is a quadratic expression in variables  for a couple of input and output vectors and . We didn’t request any special property of these vectors so  is a quadratic expression in variables  for every couple vectors and . Sum of quadratic expressions in variablesis a new quadratic expression in variables  and the procedure of obtaining  for more than one couple of input and output vectors is the same; simply we take:

(14)

and

(15)

where nv is the number of couples of input and output vectors.

We chose  and for each m we find as the complex number that gives the best compliance of (1), i.e. we determine the values  according to (13) and the position of fault should be in the element of the line for which the value is minimal.

Let’s note, that above described way how to obtain and the index of faulted section has pretended no presumes about vectors and ; we can understand

(16)

Where W is an arbitrary matrix of complex numbers of matrix rank N. It is easily seen after a rearrangement of (16) into:

(17)

so, we can involve for example symmetrical components into the game again.

- Numerical experiments

We assumed a 3 wire HV line of 400kV voltage and 100km length, the influence of earthing cables has been mathematically excludes so the rank of H-matrix is 6.

A set of pseudo-random input vectors has been generated for a chosen Gaussian probability distribution of random complex noise added to voltage and current phasors. For exact values of vectors a respective set of vectors has been generated by multiplying (simulated input) vectors by fault respecting H-matrix and the same noise respecting the uncertainty of phasor determining process has been added to obtain set of vectors .

The random values has been created to satisfy condition that interval of probability is of length  for the phasor’s amplitude, is the average value of the amplitude of a phasor, interval of probability is of length  for the phasor’s angle.

The line division and position of the fault have been set and for different values of ka and ru, . Results are shown on next Figs.:

Figure 2.  , fault position determined properly.

Figure 3. , fault position determined properly.

Figure 4.  , fault position determined instead of proper value

- Conclusion

Numerical experiments show that fault location method based on H-matrices can be useable if measurement accuracy of phasors is good enough. The proof of the realization of the method using a finite algorithm has been made.

References

[1]	Novotný T., Kubín P., Kyncl J.: The Influence of Measurement Accuracy  on Fault Location Method, IVth International Scientific Symposium ELEKTROENERGETIKA 2007, 19.-21. 9. 2007, Stará Lesná, Slovak Republic

ACKNOWLEDGEMENT

The financial support of the Ministry of Education, Youth and Sports of the Czech Republic (Research Plan MSM6840770017) is also highly acknowledged.